STANDARD OPERATING PROCEDURE for ETP and RO

- Use personnel protective equipment’s such as Safety helmet, safety shoes, cotton gloves (operators), pvc gloves (sludge handling) and pvc aprons.

- Collet the contamination/effluent water form STP/SCP/Hot dip galvanization and store in collection tank.

- Above water transfer into neutralization tank and neutralize the collected effluent water in neutralization tank by adding sufficient quantity of caustic lye.

- Use spent acid (lime powder) for neutralize the low Total Dissolved Solids (TDS) effluent.

- After neutralization of low TDS transfer through filter press.

- After completion of filter press activity collect the sludge in solid form and shift into the elevated platform.

- Filter press out let water passing through tube settler into RO feed tank.

- Start the RO operation with the RO feed tank water.

- Before store the RO product water check water Ph, low TDS and ensure as per the standards.

- Product water should be collect in storage RO water tank and stored RO product water feed to SCP operation.

- RO reject water again feed into second RO operation.

- Second RO product should store in RO water storage tank

- High Total Dissolved Solids water pass through filter press.

- Collected sludge cake from filter press stored at elevated platform.

- Evaporate the collected high TDS alkaline after from ETP.

- After evaporation feed water use as cooling tower makeup water and collected slots from ATFD send to Ramkey or TSDF.

SOP NO:  PIL/ETP/PM/05 REV. NO. 6   DATE: 25.08.2025